## Slide 1: Notes on PV Installation Labor

## Slide 2: Key Points
I estimate 8-10 labor hours/kilowatt (DC)
  Consistent with estimate from Renewable energy Policy Project (2001): 8 labor hours/kilowatt
  But this is still a preliminary estimate
Relevant occupations: electricians and general construction contractors
Must distinguish direct labor for installation from indirect labor/overhead; my estimate is for direct labor

## Slide 3: Methodology
Estimate labor / kW based on two “real” projects
Compare with estimates from my own bottom-up analysis
Compare with REPP (2001) data
Explain potential deviations from my estimate

## Slide 4: Project example from Sunlight Electric
System size (CEC-AC): 146 kw
System cost: $1.25 million
Sunlight Electric paid a contractor $150k for the installation work (and kept about $150k for its own costs/profit)
Sunlight Electric founder, Rob Erlichman, estimated the costs of the contractor:
  Construction took 8 weeks for a crew of 4 => 1280 labor hours in total
  Use a weighted average hourly rate per person of $25/hour => $32k in labor cost
  Estimate another $32k for equipment & insurance
  The rest ($150k-$32k-$32k = $86k) is profit for the installer
  8.76 labor-hours per kW (CEC-AC)
  or about 10.3-11.0 labor-hours per kW (DC)

## Slide 5: Other calculations
24-30 labor hours for a 2.87kW (DC) system: (www.patrickchapman.com/solar.htm) 8.4-10.5 labor hours per kW (DC)
My own estimate for a 3.96 kW (DC) system, based on RS Means Data:
Installation task | Labor per Unit (from RS Means) | Estimated Hours
Mounting rails | 2 labor hours for 6 panels | 7.3
PV Panels: 22 180W panels | 1 labor hour per panel | 22
Inverter | 4 labor hours per inverter, 1 labor hour for conduit box | 5
DC disconnect | 1 labor hour per unit | 1
Readout Panel | 2 labor hours per unit | 2
TOTAL |  | 37.3
37.3 labor hours / 3.96 kw
=
9.4 labor hours / kw (DC)

## Slide 6: Labor Estimates for Work Across the Value Chain Data from Renewable Energy Policy Project (2001)
8000 hours per MW => 8 hours per KW
Source: “The Work that Goes into
Renewable Energy”
2001, Singh & Fehrs (Renewable Energy Policy Project)

## Slide 7: Other estimates and why we should be careful with them
Energybible.com
  Total labor cost seems reasonable ($1.33 per Watt)
  But the labor hours seem high (48 hrs x 3 people = 144), and is not based on actual projects or estimates from an installer
  Does not consider overhead and profit of installer
Photon Consulting report
  Says installation labor cost per MW = $400,000
    @ $40/hr =>10 labor-hrs / kW
    @ $25/hr => 16 labor-hrs /kW
  But it does not specify the type of labor – e.g. does this include system design? Does this include permitting?
  Likely to be upwardly biased
Celtic Solar Blog
  62 labor hours to install 4kW system => 15.5 labor-hrs / kW
  But a reading of the work activities suggests that this also includes design activities.
  Likely to be upwardly biased
If we include direct labor and indirect labor/overhead, I estimate an upper bound would be approximately double my estimate of 8-10 labor hrs / kW = > 16-20 labor hrs / kW.
  Based on interview with Sunlight Electric
  Consistent with REPP (2001) data

## Slide 8: Type of labor to install a PV System

## Slide 9: Timeline of a Typical Installation
Provide potential customers general education on benefits of solar
Analysis of customer electricity usage/bill
Site visit, system design
Present proposal to customer
Sign contracts
Apply for permits from municipality, rebate from state, interconnection from utility
Collect materials, system construction
Municipality signs off, utility interconnection, final inspection for rebate
Customer asks for proposal
Customer accepts proposal
Solar system fully operational
~2 months to 2 years
Systems Integrator
Installer

## Slide 10: Systems integration & installation work activities
General education of benefits of solar – to develop interest in requesting a proposal
Then, once someone expresses interest
  Analysis of customer electricity usage/bill
  System design: e.g. which panels, inverters? Where to mount? Number of panels/size of string?
  Presentation of proposal to customer: explain impact to electricity usage, environmental impact, discuss financing mechanisms
Then, once the customer says yes
  Before construction: Sign contracts, apply for building permits, make reservations for state rebates, apply for interconnection with utility
  Secure materials & construction
  After construction: municipality to sign off permit, utility performs interconnection, final rebate inspection from state
Many tasks are not part of direct labor (construction)

## Slide 11: Skills Required for an Installation
From interview with Sunlight Electric (installer)
  “80% of the installation work is not specific to solar….requires basic construction skills”
  E.g. on a ground-mounted system
    to install posts, you dig holes & fill them with concrete
    To run wiring, you dig trenches
    You attach modules to the rails (which anyone who can operate a screwdriver or wrench can do)
Installer requirements
  General contractors’ license, or electricians’ license, or [only in CA] a solar contractors’ license
  Some states require
    that installers be certified by NABCEP (North American Board of Certified Energy Professionals), or
    that installers have some minimum amount of solar experience, or
    go through some formal training on solar installation
Work specific to solar
  Direct: Installing inverters
  Indirect: Sales, system design, applications/permits for rebate and interconnection

## Slide 12: Activities in the Direct Installation of a PV System (roof-mounted, grid-connected)
Construction Activity | Purpose
Mount rails on roof | for mounting panels
Mount PV panels on rails | for generating electricity
Install inverter | to convert DC to AC
Install DC disconnect | to disconnect system when performing repair/replacement of system components
Install AC meter | to measure the electricity output of the system
Pull wire | to connect various system components & to ground the system
Install junction box | to combine wiring from panels
A nice description, with pictures, can be found here:
http://celticsolar.blogspot.com/2007/11/first-day-of-solar-install.html